## Slide 1: Bringing Off-Shore Wind to New England's Shores
Key learnings from pioneering offshore wind transmission
Søren Hindbo, Head of Electrical Systems
Friday, June 16, 2017

## Slide 2: DONG Energy Wind Power is the global market leader in Offshore Wind
Unparalleled experience and track record
Under construction
In operation
Under development
Walney Extension
Walney 1 + 2
Westermost Rough
Isle of Man
West of Duddon Sands
Barrow
Burbo Bank Ext.
Burbo Bank
Gunfleet Sands 3
Gunfleet Sands 1 + 2
Lincs
London Array
Race Bank
Horns Rev 1 + 2
Hornsea 1
Anholt
Middelgrunden
Vindeby
Nysted
German Cluster
Borkum Riffgrund 2
Borkum Riffgrund 1
Gode Wind 1
Gode Wind 3
Gode Wind 2
Bay State Wind
21 offshore wind farms in operation
7 offshore wind farms under construction
15 Partnerships
26 years of experience and track record in the offshore wind sector
1991
2017
3,840 MW under construction
2,000 Dedicated employees
3,591 MW Constructed capacity
7.5 million Europeans with clean electricity
3,662 MW
World's leading operator
Hornsea 2 + 3 + 4
Ocean Wind
Avedøre
DONG Energy Wind Power geographical footprint
APAC
Taipei office
Borssele 1+2

## Slide 3: Key learnings from pioneering offshore wind transmission
Scope for grid connection in Europe
“HVAC vs HVDC”
Export cables
Interlink

## Slide 4: Scope of offshore grid connection in Northern Europe
Transmission System Operator | Onshore substation | Export cable | Offshore Substation |  | Array cables | Wind turbines
UK NGET | Wind Farm scope / divested to OFTO 1) |  |  |  | Wind Farm scope | 
DE TENNET FR RTE | Offshore TSO scope |  |  | Wind Farm scope |  | 
DK Energinet.dk NL TenneT | TSO scope / Offshore TSO scope |  |  |  | Wind Farm scope | 
1) Offshore Transmission Owner (3rd party)
COMPENSATION
COMPENSATION
NO COMPENSATION

## Slide 5: HVAC vs HVDC, based on Hornsea “One” 1,2 GW, 160 – 190 km
HVDC/HVAC break even between 100 – 200 km. Distance is reducing
 | HVDC (VSC) | HVAC
CAPEX | Higher | Potential for lower
OPEX | Lower, due to electrical losses, but higher maintenance costs offshore | Higher, due to electrical losses
Availability | Lower | Potential for higher
Section able | Not able to section without significant extra cost | Potentially split in 3 separate systems and stage investments

## Slide 6: Hornsea One HVAC
Hornsea One HVDC

## Slide 7: Export cable – the weakest and most expensive part
We expect 2-3 export cable faults pr. 100km pr. 20 year (CIGRÈ)
Cost of export cables are up to 60% of the transmission system
Walney 3+4 659 MW, HVAC, 2OSS, 1OnSS, 400/220/34 kV, 68+4 km (WR)

## Slide 8: Interlink between platforms
Improving wind farm availability via interlink between platforms either at High Voltage or Medium Voltage
Advantage: Export energy during export cable faults
No permanent diesel generator offshore substation will reduce HSE and fire requirements
Reduce need for diesel gen-sets at WTGs
Possibly postponing of second export cable and reducing O&M costs
Disadvantage: Additional cost for interlink: Interlink cable, switchgear for interlink cable , extra j-tubes
Onshore substation
Offshore substation
The Solution
Wind farm
High Voltage
Medium voltage
Wind farms
High Voltage interlink cable

## Slide 9: Thank you for listening!

## Slide 10: Back-up

## Slide 11: World largest Variable Shunt Reactor; 120-300MVAr, 220kV
Hornsea 1, 1218 MW, HVAC 3OSS, 1RP, 1OnSS, 400/220/34 kV 142+38 km (WR)

## Slide 12
Walney 3+4 659 MW, HVAC, 2OSS, 1OnSS, 400/220/34 kV, 68+4 km (WR)
Longest power cable pull, 3.4km of cable within the intertidal zone

## Slide 13: Onshore substation, Racebank
Race Bank 573 MW, HVAC, 2OSS, 1OnSS, 400/220/34 kV 74+12 km

## Slide 14: Offshore substation
Walney 3+4 659 MW, HVAC, 2OSS, 1OnSS, 400/220/34 kV, 68+4 km (WR)